## Slide 1: Status of HK water system and water quality 3rd Open Meeting for Hyper-K June 21 2013
1
Hiroyuki Sekiya
ICRR, University of Tokyo
for the Hyper-K Working Group 2

## Slide 2: Targets of WG2
Source water in the mountains
  Tochibora and Mozumi
Ultra pure water for supplying
  Water system design
Water in the tank
  Water flow design
Gd water option
  Mark’s talk

## Slide 3: Source Water for Hyper-K
Tochibora is already reported.
  Our demand (>300m3/h) is filled.
Mozumi is not investigated officially yet.

## Slide 4: Atotsu water stream
45
40
30
25
15
10
5
0
20
35
m3/min.

## Slide 5: In addition
More than 300m3/h spring in KAGRA tunnel

## Slide 6: Hyper-K water system Cost estimation of the Revised design

## Slide 7
Compressor
Dryer
0.3mm
filter
Buffer
H2O,CO2
remover
20oC
Charcoal
0.1mm
filter
0.01mm
filter
0.01mm
filter
-40oC
Charcoal
Buffer
10mm filter
Buffer
CO2 remover
Buffer
1mm filter
HK Tank
Rn Free Air generator (400Nm3/h)
Water Purification System
0.24kt/h for initial supply
Mine water
RO
DI(MB)
DI(CP)
UV
MD
UF
T controller
1.2kt/h for recirculation
purge
purge
purge
NO RO
Tochibora plan

## Slide 8
Compressor
Dryer
0.3mm
filter
Buffer
H2O,CO2
remover
20oC
Charcoal
0.1mm
filter
0.01mm
filter
0.01mm
filter
-40oC
Charcoal
Buffer
10mm filter
Buffer
CO2 remover
Buffer
1mm filter
HK Tank
Rn Free Air generator (400Nm3/h)
Water Purification System
0.3kt/h for initial supply
Mine water
RO
DI(MB)
DI(CP)
UV
MD
UF
T controller
1.2kt/h for recirculation
purge
purge
purge
Mozumi plan
CO2 remover
RO
DI(MB)
purge
purge
NO RO

## Slide 9: Super-K water system
reject (drain)
reject (drain)
mine water
drain
reject
Primary pump
filter
filter
RO-1 pump
RO-2
pump
RO water tank
post RO
pump
RO-2
RO-1-1
vacuum degasifier
RO-3
reject
RO-3 pump
Ion exchanger 1/2
UV
sterilizer
purified water supply pump A/B
A
B
SK
tank
ultra filter
membrane degasifier
reject
550
Rn-free-air
dissolving tank
PI-1
PI-2
PI-3
PI-8
PI-9
PI-A
PI-B
strainer
FI-1
FI-2
PI-5
PI-11
PI-18
FI-10
FI-101
PI-20
TIA-2
FI-6
FI-7
FI-204
FI-5
FI-3
FP-4
FP-5
FI-202
RT-3
RT-4
RT-2
RT-1
CIA-1
CIA-6
CIA-2
CIA-3
CIA-4
TI-101
CV-1
ID
bottom
FI-ID
CIA
CV-2
v94
700
compensation pump
strainer
UF reject tank
HE1
reject
HE3
reject
UF reject pump
return
pump
HE4
PI-C
RO-1-2
filter

## Slide 10: With or without RO?
For prolong the lifetime of UFs
  At the beginning of the recirculation, UFs may be clogged frequently.
Initial cost vs. running cost
MF
UF
NF
RO
DI

## Slide 11: Design with RO

## Slide 12: Layout
3 stages
  Room for
  Gd option

## Slide 13: Cost estimation
Difference from previous estimation
  RO
  Increased UV sterilizer
  SK-type MD
49.35 Oku-Yen

## Slide 14: Consideration of running cost
w/RO
w/o RO
Initial
cost
Running cost
About RO
After 5 years of running, w/RO system will gain cost merit.
3.5M$
0$
1.6M$
2.3M$

## Slide 15: Plumbing from water system to tanks

## Slide 16: Cost estimation
1.05 Oku-Yen

## Slide 17: Plumbing in the tanks
Cost is already included in the TANK
Additional inlets/oultels at 5 levels of side wall for:
  future activities to prevent stagnation
  recirculation during initial filling to prevent bacteria from growing (180days!)

## Slide 18: Water Flow simulation updates
One compartment for the first step
Software:
ANSYS GAMBIT2.4.1+Fluent13.0

## Slide 19: Water inlets & outlets conditions
Equally distributed per top/bottom cross section
Top and bottom pipes only

## Slide 20: ID & OD Conditions
ID & OD are dealt as completely separated containers.
 | Inner detector | Outer detector
Volume | 370,000m3 | 89,000m3
Flow rate | 96.7t/h | 23.3t/h
Number of inlets (outlets) | 18 | 4
Flow rate / inlet (outlet) | 5.37 | 5.82
  Because of its symmetrical shape, only 1/4 volume is considered for the simulation.
  1,400,000 mesh
  (xy, and yz symmetry)

## Slide 21: Temperature condition
Cooling water 10.5oC
Supplying water 13.0oC
Top level rock 16.7oC
Bottom level rock 17.7oC

## Slide 22: Other heat source conditions
Unlike SK, electronics(HV, QBee,..) are also in the tank.
The heat from compensation coil depends on the direction of the tank.
47.4kW
Area
For one compartment

## Slide 23: Full treatment simulation
This is like SK… LowE oriented tuning.
  Bottom convection and top stagnation.
Temperature
ID ¼
supply: bottom, return: top

## Slide 24: Inverse operation
This is atmpd/t2k oriented tuning.
  Whole convection uniform detector
Temperature
ID ¼
Supply cold water to the top, return: bottom

## Slide 25: Time evolution
Not yet
10 days
20 days
30 days
40 days
supply: bottom, return: top
Supply cold water to the top, return: bottom

## Slide 26: Inlet pipe shape simulation
SK inlet (thickness is unknown)
  Very difficult…
4mm thick pipe case
Thin pipe case

## Slide 27: Conclusion
Hyper-K water system was re-designed w/RO.
  For both Mozumi and Tochibora options
  Rough cost estimations are finished
Progress on the water flow simulation.
  Super-K flow is reproduced in Hyper-K tank.
  Started to estimate the effects of inlet pipe shapes.
  Working on detail simulations.
    SK flow in SK tank? For the validation of the simulation.
    Using side wall inlets/outlets

## Slide 28: SK mesh for the flow simulation