## Slide 1: Status of HK Water 4th Open Meeting for Hyper-K January 28 2014
1
Hiroyuki Sekiya
ICRR, University of Tokyo
for the Hyper-K Working Group 2

## Slide 2: Plumbing in the tanks
Additional inlets/outlets at 5 levels of side wall for:
  *future activities to prevent stagnation
  *recirculation during initial filling to prevent bacteria from growing
Slide from the last open HK meeting

## Slide 3: Topic of this talk
Make the most of the side wall inlets and outlets to go beyond SK water quality
  Current activity to prevent stagnation
    is water flow simulations
  Recirculation during initial filling
    requires additional bottom pumps

## Slide 4: Water Flow simulation
One compartment
Software updates:
ANSYS GAMBIT2.4.6+Fluent14.5

## Slide 5: ID & OD Conditions
ID & OD are dealt as completely separated containers.
 | Inner detector | Outer detector
Volume | 370,000m3 | 89,000m3
Flow rate | 96.7t/h | 23.3t/h
Number of inlets (outlets) | 18 | 4
Flow rate / inlet (outlet) | 5.37t/h | 5.82t/h
  Because of its symmetrical shape, only 1/4 volume is considered for the simulation.
  1,400,000 mesh
  (xy, and yz symmetry)
Reminder

## Slide 6: Water inlets & outlets conditions
Equally distributed per top/bottom cross section
Top and bottom
Reminder
ID
OD

## Slide 7: Heat source conditions
47.4kW
Area
For one compartment
Base on measured Tochibora temperature
Cooling water 10.5oC
Supplying water 13.0oC
Top level rock 16.7oC
Bottom level rock 17.7oC
Reminder

## Slide 8: SK-like operation
  Reproduces SK
    bottom convection & top stagnation
Temperature
ID ¼
supply: bottom, return: top
Reminder static solutions
→LowE oriented tuning.

## Slide 9: Inverse operation
  Whole convection
    uniform detector
Temperature
ID ¼
Supply cold water to the top, return: bottom
→T2HK oriented tuning.
Reminder static solutions

## Slide 10: Water replacement efficiency
10 days
20 days
30 days
40 days
supply: bottom, return: top
Not yet
supply cold water to the top, return: bottom
30%
50%
65%
75%
40%
60%
75%
85%
15%
45%
55%
75%
w/ Time evolution

## Slide 11: Try to maximize the efficiency using the side wall pipes
Two more cases

## Slide 12: Comparison with “SK operation”
10 days
20 days
30 days
40 days
40%
60%
75%
85%
15%
45%
55%
75%
30%
30%
25%
45%
55%
60%
70%
75%
80%

## Slide 13: Comparison with “SK operation”
10 days
20 days
30 days
40 days
40%
60%
75%
85%
15%
45%
55%
75%
35%
20%
40%
55%
60%
70%
70%
80%

## Slide 14: Milder temperature gradient
Suppresses the bottom convection region and enlarges lowest energy FV
286.1K
286.2K
286.3K

## Slide 15: 90 days to fill a tank

## Slide 16: 60 days filling without recirculation caused
2 months dead + 2 months bad (for lowE)
SK-I
SK-III
Water transparency [ m ]

## Slide 17: HK has 2 recirculation systems
One is used for the filling, the other can be used for the purification of the filled water!

## Slide 18: New bottom pump
Pump for circulation during the filling period
To 2nd stage
From 2nd stage
Side wall outlets for this level
HK Tank
Water level
Main return pump
Additional pumps should be installed at the bottom

## Slide 19: Now pump rooms
L3.4m x W3.7m x 6 must be allocated somewhere near the tanks.

## Slide 20: Conclusion
Progress on the water flow simulation.
  Using side wall inlets/outlets
Started designing the recirculation mode during the initial filling
  Additional pump rooms should be caverned

## Slide 21: おまけ

## Slide 22: But there is no pump that can suck 48m of water
Pumps should be installed at the bottom
Like LBNE CDR
arXiv: 1204.2295